## Sheet1
Discharge Velocities for Cambridge Heaters
with Standard Discharge Accessories
Discharge velocity is a critical function of a heater's being able to properly distribute heat throughout a building. The air entrainment resulting from the higher discharge velocities of the S-Series heaters is one reason why the temperature differences from front to back and from floor to ceiling are typically within 3°-5°.
Discharge
| Model | Airflow* (cfm) | Area (ft2) | Velocity (fpm) |  | Inlet
| SA250 | 1565.2174 | 0.58681 | 2667.3527 |  | 1200
| SA350 | 2113.0435 | 0.58681 | 3600.9262 |  | 1620
| S400 | 3032.6087 | 1.6806 | 1804.5275 |  | 2250
| S800 | 4717.3913 | 1.6806 | 2807.0428 |  | 3500
| S950 | 6739.1304 | 2.5208 | 2673.3741 |  | 5000
| S1200 | 7817.3913 | 3.6 | 2171.4976 |  | 5800
| S1600 | 9353.913 | 3.6 | 2598.3092 |  | 6940
| S1850 | 13478.2609 | 5.0417 | 2673.3741 |  | 10000
| S2200 | 15114 | 6.9 | 2190.4348 |  | 12500
| S3200 | 19408.6957 | 6.9 | 2812.8544 |  | 14400
| M110 w/3 way plenum | 3000 | 6.8 | 441.1765
| M110 w/4 way plenum | 3000 | 6 | 500
| M110 w/3 way diffuser | 3000 | 4 | 750
| M110 w/4 way diffuser | 3000 | 5.01 | 598.8024
| M112 w/3 way plenum | 4200 | 7.65 | 549.0196
| M112 w/4 way plenum | 4200 | 6.88 | 610.4651
| M112 w/3 way diffuser | 4200 | 3.95 | 1063.2911
| M112 w/4 way diffuser | 4200 | 5 | 840
| M115 w/3 way plenum | 7500 | 9.93 | 755.287
| M115 w/4 way plenum | 7500 | 11.56 | 648.7889
| M115 w/3 way diffuser | 7500 | 6.44 | 1164.5963
| M115 w/4 way diffuser | 7500 | 8.11 | 924.7842
| M118 w/3 way plenum | 11000 | 14.71 | 747.7906
| M118 w/4 way plenum | 11000 | 18.32 | 600.4367
| M118 w/3 way diffuser | 11000 | 8.24 | 1334.9515
| M118 w/4 way diffuser | 11000 | 10.3 | 1067.9612
| M120 w/3 way plenum | 18000 | 22.75 | 791.2088
| M120 w/4 way plenum | 18000 | 24.48 | 735.2941
| M120 w/3 way diffuser | 18000 | 11.2 | 1607.1429
| M120 w/4 way diffuser | 18000 | 14 | 1285.7143
| M125 w/3 way plenum | 27000 | 34.44 | 783.9721
| M125 w/4 way plenum | 27000 | 36.72 | 735.2941
| M125 w/3 way diffuser | 27000 | 16.4 | 1646.3415
| M125 w/4 way diffuser | 27000 | 20.5 | 1317.0732
| M130 w/3 way plenum | 38000 | 45.84 | 828.9703
| M130 w/4 way plenum | 38000 | 55.08 | 689.9056
| M130 w/3 way diffuser | 38000 | 23.12 | 1643.5986
| M130 w/4 way diffuser | 38000 | 28.9 | 1314.8789
| M136 w/3 way plenum | 50000 | 55.08 | 907.7705
| M136 w/4 way plenum | 50000 | 73.44 | 680.8279
| M136 w/3 way diffuser | 50000 | 26 | 1923.0769
| M136 w/4 way diffuser | 50000 | 38 | 1315.7895
| M140 w/3 way plenum | 75000 | 122.72 | 611.1473
| M140 w/4 way plenum | 75000 | 163.45 | 458.8559
| M140 w/3 way diffuser | 75000 | 32.6 | 2300.6135
| M140 w/4 way diffuser | 75000 | 51.5 | 1456.3107
* Discharge airflow at maximum rated temperature rise
Formulae:
|  | Airflow (cfm) / | Area (ft2) = | Velocity (fpm)
|  | 50000 | 100 | 500
| Airflow / | Height (in) / | Width (in) |  | Velocity (fpm)
| 50000 | 120 | 120 | x 144 = | 500
Model | Airflow (cfm) | Area (ft2) | Velocity (fpm)
M110 w/o | 3000 | 1.2 | 2500
M112 w/o | 4200 | 1.7 | 2470.5882
M115 w/o | 7500 | 1.7 | 4411.7647
M118 w/o | 11000 | 2.4 | 4583.3333
M120 w/o | 18000 | 4.2 | 4285.7143
M125 w/o | 27000 | 6.7 | 4029.8507
M130 w/o | 38000 | 9.3 | 4086.0215
M136 w/o | 50000 | 12.6 | 3968.254